## 500XL3
Zurn Wilkins Model 500XL3(F) |  |  | System Data (Inputs) |  |  |  | PRV Station Configuration Suggestions (Results) |  |  |  | 500XL3 falloff | [6 empty] | Yes (100%) | Yes
|  |  | Flow Rate* | Minimum (GPM) |  | 0 | Low flow By-pass required |  | No | Flow Rate | 1" | 1-1/4" | 1-1/2" | 2" | 2-1/2" | 3" | 4" | Yes (partial) | No
|  |  |  | Maximum (GPM) |  | 300 | Parallel PRV quantity |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | No
|  |  | Pressure Reduction* | Inlet (Supply) Pressure |  | 140 | Multi-stage reduction required |  | No | 5 | 0.43 | 0.35 | 1.04 | 0.26 | 0.2 | 0.5 | 0.5
|  |  |  | Desired System (Outlet) Pressure |  | 60 | Series PRV quantity |  | 1 | 10 | 0.78 | 1.05 | 1.88 | 0.48 | 0.36 | 0.93 | 0.93
[10 empty] | 15 | 1 | 1.73 | 2.55 | 0.67 | 0.49 | 1.33 | 1.2028
|  |  | Accessories |  |  |  | Total PRV count suggested |  | 1 | 20 | 1.14 | 2.19 | 3.09 | 0.83 | 0.61 | 1.67 | 1.3365
|  |  | System pressure monitor (sensor) required? |  |  | No | PRV reduction ratio |  | 2.3333 | 25 | 1.44 | 2.45 | 3.5 | 0.96 | 0.7 | 1.98 | 1.485
[7 empty] | Suggested configuration |  | 1BF | 30 | 2.23 | 2.69 | 3.83 | 1.08 | 0.77 | 2.25 | 1.65
|  |  | *Click "Button" Below to refresh image after changing inputs* | [6 empty] | 35 | 4.01 | 3.33 | 4.09 | 1.18 | 0.83 | 2.49 | 1.815
[7 empty] | PRV Size (Inches) |  | Fall-off (PSI) @ Maximum Flow Rate | 40 | 7.4 | 4.95 | 4.32 | 1.28 | 0.88 | 2.69 | 1.9965
500XL3 Product Specifications | [6 empty] | 4 |  | 8.5714 | 45 | 13.19 | 8.34 | 4.53 | 1.37 | 0.92 | 2.87 | 2.1962
Max Working Inlet Pressure (PSI) |  | 400 | *Note: figure is only a representation of the system and may vary in detail between each application.* | [6 empty] | 50 | 22.26 | 14.5 | 4.77 | 1.46 | 0.95 | 3.01 | 2.4158
Max Water Temperature (F) |  | 140 |  |  |  |  | Instructions |  |  | 55 |  | 24.59 | 5.04 | 1.56 | 0.99 | 3.14 | 2.5
Max Reduced Pressure Setting (PSI) |  | 125 |  |  |  |  | 1) Enter the value for the min. & max. flow rates for the plumbing system being designed. (If the minimum flow is unknown, leave blank or enter "0"). |  |  | 60 |  |  | 5.39 | 1.67 | 1.02 | 3.24 | 2.6195
Min Reduced Pressure Setting (PSI) |  | 15 | [7 empty] | 65 |  |  | 5.83 | 1.79 | 1.05 | 3.33 | 2.7447
Minimum Flow Rate (GPM) |  | 0 |  |  |  |  | 2) Enter the value for the system's inlet pressure and the desired outlet pressure. |  |  | 70 |  |  | 6.4 | 1.93 | 1.09 | 3.4 | 2.8759
[7 empty] | 3) Select "Yes" or "No" for the pressure monitor in the Accessories section. |  |  | 75 |  |  | 7.12 | 2.1 | 1.13 | 3.45 | 3.0134
Suggested Accessories | [6 empty] | 4) Click the "Display Schematic Diagram" button and refer to the image below for a visual representation of the the "Suggested Configuration" for individual PRV, or PRV station. |  |  | 80 |  |  | 8.01 | 2.3 | 1.19 | 3.49 | 3.1574
'Y' Option (Wye Strainer) | [9 empty] | 85 |  |  | 9.1 | 2.53 | 1.25 | 3.53 | 3.3083
[10 empty] | 90 |  |  | 10.43 | 2.8 | 1.33 | 3.55 | 3.4665
[7 empty] | Notes |  |  | 95 |  |  | 12.01 | 3.12 | 1.42 | 3.56 | 3.6322
Legend | [6 empty] | This program will specify the proper sizing and quantities of 500XL3 valves required, based on specified pressure settings & flow characteristics input into cells 'I2' through 'I5'. |  |  | 100 |  |  | 13.87 | 3.48 | 1.53 | 3.58 | 3.8058
Configuration. | Description | [8 empty] | 105 |  |  | 16.04 | 3.9 | 1.65 | 3.58 | 3.9877
1B(F) | One Bronze (Flanged) PRV | [5 empty] | Max. flow rate suggested for each valve size matches typical 8ft/sec. plumbing velocity limit. |  |  | 110 |  |  |  | 4.37 | 1.79 | 3.59 | 4
2B(F) | Two Bronze (Flanged) PRVs | [5 empty] | Due to highly efficient flow performance, do not use a standard 500XL3 as a low flow bypass, only use the 500XL3BPK or 500XL3DUBP w/ bypass tailpiece as low flow bypass valve options. |  |  | 115 |  |  |  | 4.91 | 1.95 | 3.59 | 4.08
2B-L | Two Bronze PRVs, w/ low-flow by-pass | [8 empty] | 120 |  |  |  | 5.51 | 2.14 | 3.6 | 4.1616
4B-L | Four Bronze PRVs, w/ low-flow by-pass | [5 empty] | Fall-off is a drop in valve outlet pressure when flowing. |  |  | 125 |  |  |  | 6.19 | 2.34 | 3.6 | 4.2448
[10 empty] | 130 |  |  |  | 6.95 | 2.56 | 3.61 | 4.3297
Product Data Links | [9 empty] | 135 |  |  |  | 7.79 | 2.81 | 3.63 | 4.4163
Click for: 500XL3 Spec. Sheet |  | Click for: 500XL3(F)(BP) (Flanged) Spec. Sheet |  |  | Click for: 1" - 2" Installation/Maint. Instructions |  |  | Click for: 2-1/2", 3" & 4" Installation /Maint. Instructions |  | 140 |  |  |  | 8.71 | 3.08 | 3.64 | 4.5046
[10 empty] | 145 |  |  |  | 9.73 | 3.38 | 3.67 | 4.5947
[10 empty] | 150 |  |  |  | 10.85 | 3.7 | 3.7 | 4.6866
[10 empty] | 155 |  |  |  | 12.06 | 4.04 | 3.74 | 4.7804
[10 empty] | 160 |  |  |  | 13.38 | 4.41 | 3.79 | 4.876
[10 empty] | 165 |  |  |  | 14.82 | 4.8 | 3.85 | 4.9735
[10 empty] | 170 |  |  |  |  | 5.22 | 3.92 | 5.073
[10 empty] | 175 |  |  |  |  | 5.65 | 4 | 5.1744
[10 empty] | 180 |  |  |  |  | 6.11 | 4.09 | 5.2779
[10 empty] | 185 |  |  |  |  | 6.6 | 4.19 | 5.3835
[10 empty] | 190 |  |  |  |  | 7.1 | 4.31 | 5.5
[10 empty] | 195 |  |  |  |  | 7.63 | 4.44 | 5.654
[10 empty] | 200 |  |  |  |  | 8.17 | 4.58 | 5.8123
[10 empty] | 205 |  |  |  |  | 8.74 | 4.73 | 5.9751
[10 empty] | 210 |  |  |  |  | 9.32 | 4.9 | 6.1424
[10 empty] | 215 |  |  |  |  | 9.92 | 5.08 | 6.3143
[10 empty] | 220 |  |  |  |  | 10.53 | 5.27 | 6.4911
[10 empty] | 225 |  |  |  |  | 11.15 | 5.48 | 6.6729
[10 empty] | 230 |  |  |  |  | 11.78 | 5.7 | 6.8597
[10 empty] | 235 |  |  |  |  | 12.43 | 5.94 | 7.0518
[10 empty] | 240 |  |  |  |  | 13.08 | 6.19 | 7.2493
[10 empty] | 245 | [5 empty] | 6.45 | 7.4522
[10 empty] | 250 | [5 empty] | 6.73 | 7.6609
[10 empty] | 255 | [5 empty] | 7.01 | 7.8754
[10 empty] | 260 | [5 empty] | 7.32 | 8
[10 empty] | 265 | [5 empty] | 7.63 | 8.16
[10 empty] | 270 | [5 empty] | 7.96 | 8.3232
[10 empty] | 275 | [5 empty] | 8.31 | 8.4897
[10 empty] | 280 | [5 empty] | 8.66 | 8.6595
[10 empty] | 285 | [5 empty] | 9.03 | 8.8326
[10 empty] | 290 | [5 empty] | 9.4 | 9.0093
[10 empty] | 295 | [5 empty] | 9.79 | 9.1895
[10 empty] | 300 | [5 empty] | 10.2 | 9.3733
[10 empty] | 305 | [5 empty] | 10.61 | 9.5607
[10 empty] | 310 | [5 empty] | 11.03 | 9.752
[10 empty] | 315 | [5 empty] | 11.46 | 9.947
[10 empty] | 320 | [5 empty] | 11.91 | 10 | 4" 8ft/sec = 318 GPM
[10 empty] | 325 | [5 empty] | 12.36 | 10.255
[10 empty] | 330 | [5 empty] | 12.82 | 10.5165
[10 empty] | 335 | [5 empty] | 13.29 | 10.7847
[10 empty] | 340 | [5 empty] | 13.77 | 11.0597
[10 empty] | 345 | [5 empty] | 14.25 | 11.3417
[10 empty] | 350 | [5 empty] | 14.75 | 11.6309
[10 empty] | 355 | [5 empty] | 15.25 | 11.9275
[10 empty] | 360 | [5 empty] | 15.76 | 12.2317
[10 empty] | 365 | [5 empty] | 16.27 | 12.5436
[10 empty] | 370 | [5 empty] | 16.79 | 12.8634
[10 empty] | 375 | [6 empty] | 13.1914
[10 empty] | 380 | [6 empty] | 13.5278
[10 empty] | 385 | [6 empty] | 13.8728
[10 empty] | 390 | [6 empty] | 14
[10 empty] | 395 | [6 empty] | 14.3612
[10 empty] | 400 | [6 empty] | 14.7317
[10 empty] | 405 | [6 empty] | 15.1118
[10 empty] | 410 | [6 empty] | 15.5017
[10 empty] | 415 | [6 empty] | 15.9016
[10 empty] | 420 | [6 empty] | 16.3119
[10 empty] | 425 | [6 empty] | 16.7327
[10 empty] | 430 | [6 empty] | 17.1644
[10 empty] | 435 | [6 empty] | 17.6073
[10 empty] | 440 | [6 empty] | 18.0615
[10 empty] | 445 | [6 empty] | 18.5275
[10 empty] | 450 | [6 empty] | 19.0055
[10 empty] | 455 | [6 empty] | 19.4959
[10 empty] | 460 | [6 empty] | 20
[10 empty] | 465 | [6 empty] | 20.66
[10 empty] | 470 | [6 empty] | 21.3418
[10 empty] | 475 | [6 empty] | 22.0461
[10 empty] | 480 | [6 empty] | 22.7736
[10 empty] | 485 | [6 empty] | 23.5251
[10 empty] | 490 | [6 empty] | 24.3014
[10 empty] | 495 | [6 empty] | 25.1034
[10 empty] | 500 | [6 empty] | 25.5
Suggested Configuration

## 5 (hidden)
Figure 1
Figure 2
Figure 3
Figure 4
Figure 5
Figure 6
Figure 7
Figure 8
Figure 9
Error: Please contact manufactor on given specifications. Outlet Pressure may not be achieved with given flow.Alternate methods may be required. Please see ACV.